CAUTION: READ INSTRUCTIONS THOROUGHLY BEFORE OPERATION OF UNIT

Ozone Generator

Operation  Manual

Ozone generator

Installation and maintenance

A: shipment

Check that the unit hasn’t been damaged during transport. Report any sign of damage to us. The generator has been tested before shipping. Read the complete guide before starting the installation.

B: System Overview

An electrostatic filter treats solid particle contaminants within the air flow.Therefore, the filter is able to remove a proportion of the odour generated by the cooking process. The remaining odour is a gas that needs to be treated with a very strong neutralizer. Ozone is a well-known powerful disinfectant which will mitigate odour from the kitchen exhaust system. 
The generator ozone outlet is connected to the exhaust duct after the exhaust hood. The ozone needs a minimum contact time with the odour to be able to change its structure and destroy it. Two seconds is the ideal timing. 
The ozone generator can be installed without an electrostatic filter if the cooking only generates grease mist (no smoke). The ozone breaks down the grease and odour by oxidation.

OZONE - AN ENVIRONMENT FRIENDLY AND NATURAL WAY OF AIR CLEANING 
The ozone generator changes oxygen molecules (O2) as found in the air we breathe to ozone (O3). Ozone is an unstable gas and, depending on temperature, reverts back to oxygen in about 10-20 minutes. Ozone in contact with the odour molecule will oxidise the odour molecule and will reduce back to oxygen. Hence, only oxygen will be exhausted.

Ozone Generator panel key instructions

A:Local time setting

B:On/off timer

C:Ozone concentration indicator

D:Working condition

Power: Turns the unit on and off

Set:Selecting mode of setting on or off timer

Hr:Setting timer’s hours

Min:Setting timer’s minutes

O3:Used to adjust Ozone concentration output

Timer setting instruction: first press Set key, upper timer blink, set local time. Second press Set key again, nether blink, set turn on/off time.

(1) The upper clock can be adjusted to the local time and used as the actual calibration time.

Press the SET key until the blinking icon is at the upper clock, you can start adjust the local timer by press Hr and Min keys.

(2) The nether clock can set on time switch under keeping turning on the power condition.

Press the SET key until the blinking icon is at the ON position, you can start adjusting Hr and Min keys respectively in turn, then start time hase been set; Next, press the SET button, the flashing icon flashes is at the OF position, you can adjust off time, the whole deligent-timer control has been completely set.

Technical specifications

| Item | Unit | QLC-20G | QLC-40G | QLC-60G |
| --- | --- | --- | --- | --- |
| Ozone output | G/Hr | 20 | 40 | 60 |
| Power | W | 180 | 350 | 380 |
| Voltage | V/Hz | AC 220V/50Hz |
| Concentration | ppm | 45 | 70 | 125 |
| Generating material | / | Ceramic plate |
| Dimension | cm | 40*30*62 |
| Unit weight | Kg | 19 | 20 | 21 |
| External case | / | Stainless steel 304 |
| Treat air flow | M3/H | ↑7000 | ↑10,000 | ↑15,000 |
| Cooling method | / | Ambient air cooling |
| Fan blower air flow | M3/H | 300 Maximum |

- The model use ceramic ozone plate with more than 10,000 hours working life;

- The model adopts discharge corona and air cooling technologies;

- Stainless steel #304 to guarantee long lifespan of this product;

- The ozone output is adjustable from 0-60g/h according to different applications;

- Programmer timer, intelligent control

- Remote control, adjustable ozone output

Note : Maximum treatment exhaust airflow indicative only, speak to your presentative prior to ordering

C. Installation Guidelines

1. Install the ozone generator on a wall with two screws. Two lags have been pre-drilled at the top of the unit.

2. The ideal installation position is in the kitchen or in the store room with easy access for servicing. Always leave the generator free of material that can restrict the unit airflow.

3. Cut one 100mm hole in the exhaust duct side or top, as close as possible to the exhaust hood outlet or after the ESP filtration unit(if included). Fit a PVC 90 mm flange in the hole. Connect the duct flange to the generator ozone outlet with a 90mm PVC plumbing pipe. Seal the pipe with the recommended glue.

4. A maximum of eight meters of  PVC pipe is recommended.

5. Plug the generator electrical lead to a power point. Press the POWER Button,when the exhaust fan switch is activated, Press the switch O3 Switch to adjust the ozone output.

6. The kitchen exhaust discharge point could be at roof or street level. Discharges should be located away from windows, doors or walkways.

7. Install a double damper as per the drawing below to be able to adjust the correct air flow and to mix the ozone with the air pollutants to achieve the best efficiency.

8.We recommend switching on the generator only when cooking occurs.

D. Suggested specification

Exhausted kitchen hood grease particles & odour shall be treated by an ozone generator QLC-Series. Efficiency of the generator shall achieve States & National Impact Assessment Criteria for Complex Mixtures of Odour Air Pollutants. The construction & installation shall meet all relevant Standards. The generator should be installed and maintained according to specifications. The generator power supply should be interlocked with the exhaust fan switch.

E. System test

1. Press power Switch,  the LCD screen  on, exhaust fan activated.

2. Adjust the ozone output for the needed level of injected ozone (0-50g/h). The LCD screen turn from Green-Blue-Red.

3. The generator is running.

4.  Preset the timer

F. Service maintenance

1. Check every month that the LCD is illuminated when the generator is on.

2. Remove the black cover on the fan air inlet and air outlet. Clean the air filters with hot water every month.

G: Warranty

Limited warranty for ozone generator. This warranty is subject to the following conditions:

a. To validate this warranty, the equipment should be installed and the end user should maintain the filter as per specifications.

b. A new air cleaner is warranted to be free from defects and /or workmanship for a period of one (1) year from the date of purchase.

c. A spare part is warranted to be free from defects and/or workmanship for a period of ninety (90) days from the date of its installation.

d. The warranty for new equipment and spare part covers the repair or replacement of the defective part.

e. To validate the warranty the end user should clean the dust filters a minimum once a month.